Guidelines

指南

Approval Process for Reduced Maintenance Frequency for Lifts installed with Remote Monitoring and Diagnostics Solution

安装远程监控和诊断解决方案的电梯减少维护频率的审批流程

1

Disclaimer免责声明

These guidelines are not a substitute for independent professional advice. These guidelines and its contents are made available on an "as is" basis, and all implied warranties are disclaimed. These guidelines are not exhaustive in covering all matters on the approval process for reduced maintenance frequency for remote monitoring and diagnostics. BCA, its employees, agents, service providers, representatives and partners shall not be liable for errors or omissions in the transmission of these guidelines, or for any claim or dispute, or liability, damage, loss or expense arising out of or relating to, or in reliance on any of the information provided in these guidelines.

这些指南不能替代独立的专业建议。 这些指南及其内容按“原样”提供，并且不承担所有默示保证。 这些指南并未详尽涵盖有关减少远程监控和诊断维护频率的审批流程的所有事项。 BCA、其员工、代理、服务提供商、代表和合作伙伴不对这些指南传输过程中的错误或遗漏负责，也不对因以下原因引起的或与之相关的任何索赔或争议、责任、损害、损失或费用承担责任： 或依赖这些指南中提供的任何信息。

Readers should seek professional legal advice if they need to determine specific legal rights and duties applicable to them. While every effort has been made to ensure that information in these guidelines is consistent with existing law and practice, BCA reserves the right to vary its position accordingly without any prior notice.

如果读者需要确定适用于自己的具体法律权利和义务，应寻求专业的法律建议。 虽然 BCA 已尽一切努力确保这些指南中的信息符合现行法律和惯例，但 BCA 保留相应改变其立场的权利，恕不另行通知。

Copyright版权

The contents of these guidelines are protected by copyright and other forms of proprietary rights, and are the property of BCA, or the party credited as the provider of the contents. You may download, view, print, and reproduce copies of these guidelines without modification for your own reference, but you shall not otherwise copy, reproduce, upload, distribute, publish, post, modify, create derivative works, transmit or in any way exploit the contents of these guidelines. If you wish to use the contents of these guidelines for any purpose other than for your own reference, please seek BCA’s prior written consent.

©Building and Construction Authority 2022

这些指南的内容受版权和其他形式的专有权利的保护，并且是 BCA 或被认定为内容提供者的财产。 您可以不加修改地下载、查看、打印和复制这些指南的副本供您自己参考，但您不得以其他方式复制、复制、上传、分发、出版、张贴、修改、创建衍生作品、传播或以任何方式利用 这些指南的内容。 如果您希望将这些指南的内容用于除供您自己参考之外的任何目的，请事先征求 BCA 的书面同意。

©建设局 2022

2

Table of Contents

1.	Introduction介绍	4

2.	Approval Process审批流程	4

3.	Stage 1: Pre-Approval Trials第一阶段：预批准试验	5

4.	Stage 2: Application Process第二阶段：申请流程	5

5.	Roles and Responsibilities角色和责任	7

6.	Flowchart on the Approval Process审批流程图	8

Annex A附录A	9

Annex B附录B	11

3

1. Introduction介绍

- In Singapore, lift owners must engage lift contractors registered with BCA to carry out monthly maintenance 1 for lifts in accordance with the maintenance requirements2 found in Part 1 of the First Schedule of the Building Maintenance and Strata Management (Lift, Escalator and Building Maintenance) Regulations 2016 (the “BMSM (LEBM) Regulations”).

在新加坡，电梯业主必须聘请与BCA注册的电梯承包商进行按月维护1，以符合《建筑维护和分层管理（电梯、自动扶梯和建筑维护）条例2016》（"BMSM (LEBM) Regulations"）第一附表第一部分中的维护要求2。

- To encourage and facilitate the adoption of Remote Monitoring & Diagnostics (“RM&D”) technologies for lifts, an interested lift owner (the “Applicant”) can now apply to the Commissioner of Buildings (the “Commissioner”) (via BCA) for approval for their lifts3 implemented with a particular RM&D solution4 to be subject to a longer maintenance interval of 3 months.

为了鼓励和促进电梯远程监控和诊断（"RM&D"）技术的采用，有兴趣的电梯业主（"申请人"）现在可以向建筑专员（"专员"）（通过BCA）申请批准，要求他们的电梯3采用特定的RM&D解决方案4，并将维护间隔延长至3个月。

- This guide aims to provide lift owners, lift service contractors and RM&D solution providers as well as other stakeholders in the lift maintenance industry more information pertaining to the application process.

本指南旨在为电梯业主、电梯维护承包商、RM&D解决方案提供商以及电梯维护行业的其他利益相关者提供有关申请过程的更多信息。

2. Approval Process审批流程

- The approval process would be in 2 Stages.

批准过程将分为两个阶段

- Stage 1: Pre-Approval Trials

第一阶段：预批准试验

- The Applicant would first have to adopt RM&D solution for their lifts in pre-approval trials.

申请人首先必须在预批准试验中采用RM&D解决方案来监控其电梯。

- The aim of the pre-approval trials process is for the Applicant to demonstrate to the Commissioner that their RM&D solution meets the requirements specified in BCA’s Code of Practice5 for Design and Performance of Remote Monitoring & Diagnostics Solution for Lifts (hereinafter referred to as “COP”).

预批准试验的目的是让申请人向建筑管理局证明其RM&D解决方案符合建筑管理局关于电梯远程监测和诊断解决方案设计和性能的实施准则（以下简称“COP”）中规定的要求。

- To demonstrate that the RM&D solution meets the requirements in the COP, the lifts installed with the RM&D solution must undergo a trial period of minimum 6 months.

为了证明RM&D解决方案符合COP中的要求，安装了RM&D解决方案的电梯必须经历至少6个月的试验期。

- At the end of 6 months, the Applicant would evaluate if the particular RM&D solution satisfies the requirements in Regulation 13A of the BMSM (LEBM) Regulations. During the 6-month pre-approval trial period, these lifts will still be required to be maintained every month by a lift service contractor in accordance with Reg 13 of the BMSM (LEBM) Regulations.

在6个月的试验期结束时，申请人将评估特定的RM&D解决方案是否满足BMSM (LEBM)法规第13A条的要求。在为期6个月的预批准试验期间，这些电梯仍需要按照BMSM (LEBM)法规第13条的规定每月由电梯维修承包商进行维护。

- The requirements for periodic maintenance of lifts can be found under Regulation 13 of the BMSM (LEBM) Regulations.

- Lift Contractors must meet a set of 20 Maintenance Outcomes stipulated in the BMSM (LEBM) Regulations that covers the critical areas of maintenance.

- Other than a home lift, vertical platform or a stairlift.

- “Remote monitoring and diagnostics solution” or “RM&D solution” means a system that (a) continuously collects data from an operating lift, (b) analyses the data to detect, diagnose and predict issues in the lift’s operation; and (c) recommends action for the lift’s maintenance.

- The COP can be found in BCA’s website: https://www1.bca.gov.sg/regulatory-info/lifts-escalators/remote-monitoring-diagnostics-for-lifts-in-singapore

4

2nd Stage – Application Process第二阶段 - 申请流程

- If the Applicant evaluates that the particular RM&D solution satisfies the requirements in Regulation 13A of the BMSM (LEBM) Regulations, the Applicant may submit an application under Regulation 13A for the lifts that had undergone the pre-approval trial process in Stage 1 to be subject to a longer maintenance interval of up to 3 months. To this end, the Applicant must complete the application using the requisite form, and prepare the necessary documents and forms to be submitted to the Commissioner.

如果申请人评估认为特定的RM&D解决方案符合《建筑维护和分层管理（升降机、扶梯和建筑维护）条例2016》第13A条的要求，则申请人可以根据第13A条提交申请，要求经过第一阶段的预批准试验的电梯可以每3个月进行一次维护。为此，申请人必须填写规定的申请表格，并准备好需要提交给专员的必要文件和表格。

3. Stage 1: Pre-Approval Trials第一阶段：预批准试验

- This section provides more information on the process of the Stage 1 pre-approval trials.

本节提供有关第一阶段预批准试验流程的更多信息。

- Applicants who are interested to conduct pre-approval trials in Stage 1 should write to BCA for a consultation with the required information (listed in Annex A) on the details of their RM&D solution.

对于有意进行第一阶段预批准试验的申请人，应向BCA提出申请，并提供有关其RM&D解决方案详细信息的所需信息（见附录A）。

- If the Applicant’s RM&D solution is assessed to be suitable after the consultations with BCA, the Applicant can proceed to conduct the pre-approval trials.

如果经过与BCA的咨询后，申请人的RM&D解决方案被评估为合适，申请人可以继续进行预批准试验。

- During the 6-month pre-approval trials, the Applicant should:

在为期6个月的预批准试验期间，申请人应该：

  - collect evidence and data, contained in documents, that demonstrate that the RM&D solution is able to meet the monitoring outcomes requirements in Table 1 listed under section 3.7.2 of the COP. The monitoring outcomes describe the lift systems that are required to be monitored and the expectations on the outcome of the monitoring;

收集证据和数据，以文件形式呈现，证明RM&D解决方案能够满足COP第3.7.2节下列的表1中的监测结果要求。监测结果描述了需要监测的电梯系统以及对监测结果的期望；

  - collect and submit information to the Commissioner on the RM&D performance indicators6 , maintenance findings7 and servicing reports monthly; and

每月收集并向专员提交关于RM&D性能指标6、维修结果7和维修报告的信息；

  - facilitate audits by the Commissioner for the lifts deployed under the trial during the pre-approval trial period. The lift service contractors engaged to maintain the lifts under the trial must facilitate and assist the Commissioner in any audit inspections that may be required by the Commissioner. The Commissioner will provide advance written notice of such audit inspections.

在预批准试验期间，为试验中部署的电梯提供专员的审核。参与试验期间电梯维护的电梯服务承包商必须在专员要求进行审核检查时提供便利并协助专员进行审核。专员将提前书面通知此类审核检查。

4. Stage 2: Application Process第二阶段：申请流程

- This section provides more information on the Stage 2 Application Process.

本节提供有关第2阶段申请流程的更多信息。

- The application must be made by the owner of the lifts installed with the RM&D solution (“RM&D Lifts”). To apply, the Applicant would need to download and fill up the requisite application, supporting forms and relevant documents, and submit them to the Commissioner. The application must set out the list of RM&D Lifts and

- For further details on the Performance Indicators, please refer to the COP.

- Data templates would be provided to the Applicant. The Applicant would have to fill in the necessary data fields and submit them to BCA monthly.

5

be endorsed by the lift service contractor engaged to maintain the RM&D Lifts as well as the intended RM&D solution provider. The list of forms is listed below and can be found on BCA’s website at https://www1.bca.gov.sg/regulatory-info/lifts-escalators/remote-monitoring-diagnostics-for-lifts-in-singapore:

申请必须由安装了RM&D解决方案的电梯的业主（“RM&D电梯”）进行。申请人需要下载并填写所需的申请表、支持表格和相关文件，并将其提交给专员。申请必须列出RM&D电梯的清单，并得到维护RM&D电梯的电梯服务承包商和拟定的RM&D解决方案提供商的认可。下面列出了表格清单，可在BCA的网站https://www1.bca.gov.sg/regulatory-info/lifts-escalators/remote-monitoring-diagnostics-for-lifts-in-singapore找到：

  - Application to Maintain Lifts using RM&D solutions at reduced maintenance frequency.

使用RM&D解决方案降低维护频率的电梯维护申请表。

  - Form A: Details of Lifts

A表：电梯详细信息表。

  - Form B: Details of Performance Indicators Values (Past 6 months)

B表：性能指标数值详情（过去6个月）。

  - Form C: RM&D Maintenance Findings (Past 6 months)

C表：RM&D维护发现（过去6个月）。

  - Form D: Checklist for monitoring outcomes for BCA’s Code of Practice for

Design and Performance of Remote Monitoring & Diagnostics Solutions for Lifts

D表：BCA关于电梯远程监控与诊断解决方案设计和性能的最佳实践的监控结果清单

- In evaluating the application, the COB must be satisfied of all of the following:

在评估申请时，建筑管理专员必须对以下所有要求感到满意：

  - that the RM&D solution can collect data on all or most of the maintenance requirements referred to under regulation 13 of the BMSM Regulations

RM&D 解决方案能够收集有关 BMSM 法规第13条规定的所有或大部分维护要求的数据。

  - the RM&D solution can predict issues8 in the operation of the RM&D Lifts;

RM&D 解决方案能够预测 RM&D 电梯运行中的问题。

  - the lift owner, lift service contractor and RM&D solution provider agree to comply with any condition imposed by the Commissioner for the approval;

电梯业主、电梯服务承包商和 RM&D 解决方案提供商同意遵守委员会对批准所附加的任何条件。

  - given the use of the RM&D solution, the appropriate frequency to carry out maintenance works for the RM&D Lifts; and

鉴于使用 RM&D 解决方案，对 RM&D 电梯进行维护工作的适当频率。

  - public safety

公共安全

- Upon written approval of the application by the Commissioner, the lift service contractor may then carry out maintenance works at the approved frequency for the RM&D Lifts, subject to the conditions of approval as may be imposed by the Commissioner.

在委员的书面批准下，电梯维保承包商可以按照批准的频率对RM&D电梯进行维保工作，但须遵守委员可能规定的批准条件。

- In approving the application, the Commissioner may impose conditions of approval which may include one or more of the following:

在批准申请时，委员可以附加一项或多项以下的批准条件：

  - the Applicant shall continue to use the RM&D solution throughout the period of approval;

申请人在批准期间必须继续使用RM&D解决方案；

  - the Applicant shall notify BCA in writing if the lift owner, lift service contractor or RM&D solution provider intends to terminate the use of the RM&D solution or wish to revert back to the monthly maintenance regime for the RM&D Lifts, and obtain the Commissioner’s approval before such termination or reversion;

如若电梯业主、电梯服务承包商或RM&D解决方案提供商有意终止使用RM&D解决方案或希望恢复到RM&D电梯的每月维护制度，申请人应书面通知BCA，并在终止或恢复之前获得Commissioner的批准。

  - the Applicant continues to ensure that the approved RM&D Lifts meet the performance benchmarks in Error! Reference source not found. at all times;

申请人需确保批准的RM&D电梯始终满足错误！找不到参考来源。中规定的性能基准要求。

  - the Application immediately notifies the Commissioner in writing as soon as the Applicant becomes aware of any defects or issues in the RM&D solution that could cause severe unintended consequences affecting public safety;

申请人在察觉到RM&D解决方案中可能导致严重意外后果影响公共安全的任何缺陷或问题时，应立即以书面形式通知委员会。

  - the Applicant shall submit data on all maintenance findings, servicing reports and performance indicator results for the RM&D Lifts to BCA on a monthly basis;

申请人应每月向BCA提交有关RM&D Lifts的所有维护发现、维修报告和性能指标结果的数据。

  - the Applicant shall ensure that the lift service contractor engaged to maintain the RM&D lifts carries out actions recommended by the RM&D

8 To demonstrate this, the Applicant must ensure that performance indicator values submitted in Form B meet the requirements in Annex B.

6

solution provider, within the timelines suggested by the RM&D solution provider; and/or

申请人应确保负责维护RM&D Lifts的电梯维修承包商按照RM&D解决方案提供商建议的时间表执行建议的行动。

  - the Applicant shall facilitate audits by BCA for the RM&D Lifts by ensuring that the lift service contractor engaged to maintain the RM&D Lifts facilitates and assists BCA in any audit inspections that may be required by BCA with advance written notice of such audit inspections.

申请人应确保负责维护RM&D Lifts的电梯维修承包商在BCA要求进行审核检查时，提前书面通知并配合BCA进行审核检查

- Roles and Responsibilities角色和责任

- Lift owners, lift service contractors and RM&D solution providers are reminded of their respective roles and responsibilities in deploying the RM&D solution for the RM&D Lifts under a longer maintenance frequency.

提醒电梯业主、电梯维修承包商和RM&D解决方案提供商，他们在实施RM&D解决方案并将其应用于RM&D Lifts的长周期维护中所扮演的各自角色和责任。

Lift Owners

- In the event that the owner finds that any of the RM&D Lifts are unsafe through information from the RM&D solution or otherwise, the lift owner should put the lift(s) out of operation immediately, alert the lift maintenance contractor and RM&D solution provider. Observations, before and after rectifications, should be recorded and logged in the RM&D data submission templates provided by BCA.

如果电梯业主通过RM&D解决方案或其他途径发现任何RM&D Lifts存在安全问题，应立即停用该电梯，通知电梯维修承包商和RM&D解决方案提供商。在进行整改前后，应记录和记录观察结果，并使用BCA提供的RM&D数据提交模板进行记录。

- The approval granted by the Commissioner provides flexibility for an extended, condition-based maintenance regime. Notwithstanding any approval granted by the Commissioner, the lift owner should take advice from the lift maintenance contractor to impose a more frequent maintenance regime, should the need arise, on any of the RM&D Lift(s).

委员批准的批准提供了更灵活的、基于条件的维护制度。尽管委员批准了任何批准，但如果需要，在任何RM&D Lifts上，电梯业主应征求电梯维修承包商的意见，并实施更频繁的维护制度。

Lift Service Contractor电梯维修服务承包商

- The lift service contractor would need to increase monitoring and is expected to respond expediently and accordingly if the lift service contractor is informed, through the RM&D Solution, the RM&D Solution Provider or otherwise, that the RM&D Lifts require intervention.

电梯维修承包商需要加强监控，并在通过RM&D Solution、RM&D Solution Provider或其他途径获知需要干预的RM&D Lifts时，做出迅速和相应的响应。

- Observations and rectification actions during intervention trips should be recorded and logged. In an event the lift maintenance contractor finds the anomalies or recommendations raised by the RM&D solution does not warrant interventions, justifications are to be clearly provided.

- 在干预行程中，应记录和记录观察和整改措施。如果电梯维修承包商发现RM&D Solution提出的异常或建议不需要干预，应清楚提供理由。

- The lift maintenance contractor should advise the lift owner as well as the RM&D solution provider on a suitable maintenance frequency/plan if the maintenance arrangements cannot meet the necessary maintenance requirements for the RM&D Lifts to operate in a safe manner.

如果维修安排无法满足RM&D Lifts的必要维修要求以确保安全运行，电梯维修承包商应向电梯业主和RM&D解决方案提供商提供适当的维修频率/计划建议。

RM&D Solution Provider RM&D解决方案提供商

- The RM&D solution provider must take the necessary precautions to prevent unauthorized control of and access to the RM&D Lifts remotely. There should be consideration in the RM&D system design minimally to log, trace, and interrupt hijacking and hacking attempts.

RM&D解决方案提供商必须采取必要预防措施，以防止未经授权的远程控制和访问RM&D Lifts。在RM&D系统设计中，应至少考虑记录、跟踪和中断劫持和黑客攻击企图。

- The RM&D solution provider has the responsibility to safeguard the RM&D Lifts’ data, regardless of storage means. The RM&D Lifts’ data must be identifiable and

7

extracted in a readable format, and be able to be provided to BCA and the lift owner upon request (in addition to the monthly data submissions to BCA, if applicable).

无论存储手段如何，RM&D解决方案提供商都有责任保护RM&D Lifts的数据。RM&D Lifts的数据必须可识别并以可读格式提取，并能够根据请求提供给BCA和电梯业主（除了适用的每月数据提交给BCA之外）。

- The RM&D solution provider should at all times work with the lift maintenance contractor, as well as lift owner, if necessary, to continuously improve the diagnostic capabilities, raising diagnostic and predictive accuracies through means of on-site validation for feedback to the RM&D Solution.

RM&D解决方案提供商应始终与电梯维保承包商合作，并在必要时与电梯业主合作，通过现场验证的方式不断提高诊断能力，提高诊断和预测准确性，并将反馈信息应用于RM&D解决方案的改进中。

6. Flowchart on the Approval Process审批流程图

- The processes from consultation to obtaining of approval are as shown in Figure 1.

从咨询到获得批准的流程如图1所示

Figure 1: Flowchart on Approval Process

- Interested applicants may request for a consultation session or send their enquiries through https://www.bca.gov.sg/feedbackform.

有兴趣的申请人可以通过https://www.bca.gov.sg/feedbackform 请求咨询会议或发送查询。

8

Annex A

- Number of lifts to be used for the pre-approval trials

预批准试验所使用的电梯数量

- Name of the RM&D solution

RM&D解决方案的名称

- Brief Description of the RM&D solution (including system architecture)

RM&D解决方案的简要描述（包括系统架构）

- Checklist for monitoring outcome

监测结果的清单

- Additional documentations and/or supporting information to demonstrate that the RM&D system meets the COP.

附加文件和/或支持信息，以证明RM&D系统符合COP要求

|  |  |  |  |  |  |  | Does the |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | RM&D system |  |  |
|  | Lift system and |  |  | Monitoring Outcomes |  |  | meet the |  |  |
|  | their sub-system |  |  |  |  |  | monitoring |  |  |
|  |  |  |  |  |  |  | outcomes? |  |  |
|  |  |  |  |  |  |  | Yes/No |  |  |
| 1. Traction |  |  |  | To be able to monitor and analyse the |  |  |  |  |  |
| Machine |  |  |  | performance of the lift and identify |  |  |  |  |  |
|  |  |  |  | potential issues with the traction machine; |  |  |  |  |  |
|  |  |  |  | and provide recommendation on possible |  |  |  |  |  |
|  |  |  |  | rectification works and indicate when they |  |  |  |  |  |
|  |  |  |  | are required. |  |  |  |  |  |
| 2. Brakes |  |  |  | To be able to monitor and analyse the |  |  |  |  |  |
|  |  |  |  | performance of the lift and identify |  |  |  |  |  |
|  |  |  |  | potential issues with the brakes; and |  |  |  |  |  |
|  |  |  |  | provide recommendation on possible |  |  |  |  |  |
|  |  |  |  | rectification works and indicate when they |  |  |  |  |  |
|  |  |  |  | are required. |  |  |  |  |  |
| 3. Suspension |  |  |  | To be able to monitor and analyse the |  |  |  |  |  |
| Means |  |  |  | performance of the lift and identify |  |  |  |  |  |
|  |  |  |  | potential issues with the suspension |  |  |  |  |  |
|  |  |  |  | means; and provide recommendations on |  |  |  |  |  |
|  |  |  |  | possible rectification works and indicate |  |  |  |  |  |
|  |  |  |  | when they are required. |  |  |  |  |  |
| 4. Guide system |  |  |  | To be able to monitor and analyse the |  |  |  |  |  |
| (i.e. guide rail and |  |  |  | performance of the lift and identify |  |  |  |  |  |
| guide shoes or |  |  |  | potential issues with the guide system; and |  |  |  |  |  |
| rollers) |  |  |  | provide recommendations on the possible |  |  |  |  |  |
|  |  |  |  | rectifications for the guide system and |  |  |  |  |  |
|  |  |  |  | indicate when they are required. |  |  |  |  |  |
| 5. Car and |  |  |  | To be able to monitor and analyse the |  |  |  |  |  |
| Landing Doors |  |  |  | performance of lift and identify potential |  |  |  |  |  |
| (including door |  |  |  | issues with the car and/or landing doors |  |  |  |  |  |
| protective devices) |  |  |  | system; and provide recommendations on |  |  |  |  |  |
|  |  |  |  | possible rectification works and indicate |  |  |  |  |  |
|  |  |  |  | when they are required. |  |  |  |  |  |
| 6. Levelling |  |  |  | To be able to monitor and analyse the |  |  |  |  |  |
| Devices |  |  |  | performance of the lift and identify |  |  |  |  |  |
|  |  |  |  | potential occurrences and instances of |  |  |  |  |  |
|  |  |  |  | mis-leveling; and provide |  |  |  |  |  |
|  |  |  |  | recommendations on possible rectification |  |  |  |  |  |
|  |  |  |  | works and indicate when they are |  |  |  |  |  |
|  |  |  |  | required. |  |  |  |  |  |

9

| 7. Fault Diagnosis | To be able to monitor and analyse the |  |  |  |
| --- | --- | --- | --- | --- |
| including the | performance of the lift and indicate if one |  |  |  |
| following | or more of the following fault(s) is/are |  |  |  |
| components: | possible cause(s) for the stoppage of the |  |  |  |
| a) Overspeed | lift: |  |  |  |
| Governor |  | Overspeed Governor Activation |  |  |
| b) Safety Gear |  | Safety Gear Activation |  |  |
| c) Controller and |  Controller and Inverter Drive |  |  |  |
| Inverter Drive |  | Failure |  |  |
| d) Buffer |  | Buffer Activation |  |  |
| e) Compensation |  | Compensation System Activation |  |  |
| System |  | Ascending Car Overspeed |  |  |
|  |  | Protection Activation |  |  |
|  |  | Unintended Car Movement |  |  |
|  |  | Protection Activation |  |  |
|  |  | Fire Emergency |  |  |
|  |  | Power Failure |  |  |
| 故障诊断，包括以下组件： a) 超速调速器 b) 安全装置 c) 控制器和逆变器驱动 d) 缓冲器 e) 补偿系统 |  | 为了能够监测和分析电梯的性能，并指示以下故障之一或多个可能是电梯停止的原因： - 超速调速器激活 - 安全装置激活 - 控制器和逆变器驱动故障 - 缓冲器激活 - 补偿系统激活 - 上行车厢超速保护激活 - 非预期车厢移动保护激活 - 火灾紧急情况 - 电力故障 |  |  |

10

Annex B

The performance indicators and benchmarks aim to provide a reference where the effectiveness of the RM&D technology can be assessed through the performance of the lifts on 3 key areas: a) safety, b) productivity, c) reliability as well as the diagnostics accuracy of the RM&D Solution.

绩效指标和基准旨在通过电梯在安全性、生产力和可靠性三个关键领域的表现以及RM&D解决方案的诊断准确性来评估RM&D技术的有效性。

Table 1:Performance Indicators and Benchmark

| Performance Indicators |  | Performance Benchmark |  |
| --- | --- | --- | --- |
| 1. | Safety – 20 Maintenance |  < 2 consecutive months of similar high-risk |  |
|  |  | findings |  |
| Outcomes安全性 - 20 维护结果 |  |  |  |
|  |  |  < 4 consecutive months of low/med risk findings |  |
| 2. | Productivity – First Time Fix | >70% for 6 months |  |
| Rate (FTFR) 生产力 - 首次修复率（FTFR） |  |  |  |
| 3. | Productivity – Mean Time to | >10% improvement |  |
| Repair (MTTR) 生产力 - 平均修复时间（MTTR） |  |  |  |
| 4. | Reliability – Technical | <0.2 (per month) |  |
| Failure Per Equipment (TFPE) 可靠性 - 单位设备的技术故障次数（TFPE） |  |  |  |
| 5. | Reliability – Uptime可靠性 - 正常运行时间 | >99% |  |
| 6. | Reliability – RM&D Device | >95% |  |
| Availability可靠性 - RM&D设备的可用性 |  |  |  |
| 7. | Diagnostics Accuracy诊断准确性 | 85% |  |

11